

# Underground Plumbing Inspection Checklist

**\*Before calling for your inspection, please make sure the following items are complete:**

**O** Township stamped plans are onsite.

**O** Pipe is installed as per specification.

**O** Drainage pipe has not been covered and is supported underneath.

**O** Drainage pipe is sloped.

**O** Cleanout has been installed where main drain exits the building. **O** Cleanouts are installed where pipe changes direction > 45 deg. **O** Floor drain(s) have been installed.

**O** Trap seal primers for floor drain P-Traps are verified.

**O** Drainage and vent piping are capped and pressurized with 5 PSI for 15 minutes (OR) drains are filled with water with a minimum water column of 10 Ft. (3m)

**O** Water supply lines are approved for underground use.

**O** Underground water supply lines are air tested to 100 PSI for 2 hrs min.

# When you have checked all applicable boxes, please email building@swox.org to book your inspection.

**We will perform the inspection within 2 business days.**